## Sheet1
100
125
1 Shift / 5 Days
2 Shift / 5 Days
3 Shift / 5 Days
3 Shift + Saturday
3 Shift + Weekend
1/32 |  | Times/Year | at | total seconds
1/16 |  | 74880 | 5 | 374400
1/8 |  |  |  | 104
3/16 |  |  |  | total hours
1/4 |  | CFM | 0
3/8 |  |  | 351.28
1/2
Timer Drain Loss Calculator |  | Change Yellow fields only
125 | Choose Compressor Pressure |  | CFM/BHP | 3.5
0.07 | Enter Power Cost ($/kWh) |  | $/CFM/Hr | 0.016217
3 Shift / 5 Days | Choose Shift |  | Hrs/Year | 6240
5 | Enter Time Off (Minutes) |  | Draining Hrs/year | 104
5 | Enter Time On (Seconds) |  | Air Drain Hrs | 93.6
10% | Percent Water Discharge
3/8 | Choose Drain Orifice |  | CFM @ Press | 351.28
533.2247 | Total Cost/Year
501 | Enter Cost of Zero Air Loss Drain
11.2748 | Payback (Months)

## Sheet2 (hidden)
Efficiency |  |  | 1 Shift / 5 Days | 2080
100 | 4 |  | 2 Shift / 5 Days | 4160
125 | 3.5 |  | 3 Shift / 5 Days | 6240
|  |  | 3 Shift + Saturday | 7488
|  |  | 3 Shift + Weekend | 8760
CFM Loss
100 | 1/32 | 1.43
100 | 1/16 | 5.74
100 | 1/8 | 22.94
100 | 3/16 | 51.62
100 | 1/4 | 91.76
100 | 3/8 | 281.02
100 | 1/2 | 367.05
CFM Loss
125 | 1/32 | 1.79
125 | 1/16 | 7.17
125 | 1/8 | 28.68
125 | 3/16 | 64.52
125 | 1/4 | 114.7
125 | 3/8 | 351.28
125 | 1/2 | 458.81